Product Introduction

Traditional miniaturized data centers have problems such as high maintenance costs, long construction time, and inability to timely understand the operating status. Prose created and innovated smart micro-data center to meet the requirements.

To meet the future deployment requirements of edge computing applications, the KHIPU Smart Microdata Center adopts a modular development concept, The advantage of low cost, suitable for customers to install quickly and put into use in time.

The Smart Microdata Center contains cabinets, power distribution systems, refrigeration systems, cabling systems, while meeting the need for continuous power, to prevent data loss, MDC can be accessed through TCP/IP, Cloud App, etc., so that customers can know the running status of the product in real time. Temperature and humidity monitoring system and air-cooling system provide suitable working environment for customers' products. It also includes face recognition, fingerprint recognition and other authentication to provide data security protection.

Main Feature

- Lower Investment by 25%

- Fast Installation Only 2H

- FC AC Energy Saving 30%

- PUE Less Than 1.26

- System Emergency Response Protection

- Biometrics Authentication

- Cascading Available for Rack

- Saving Room Space 50%

- Quiet Operation Less-than 55dB

- DCIM 24H Cloud O&M

Lead acid / Lithium battery (Battery pack)

Rack –mounted air conditioner

Rack-mounted UPS

Intelligent PDU

Rack-mounted fire suppression module (optional)

Rack-mounted power distribution box

Intelligent lock

Monitor system

Humiture & Smoke sensor

System specification

W600mm* D1200mm * H2050mm, 3 pcs of racks can be put in cascade configuration.

| Item | Standard Cabinet |
| --- | --- |
| Height Unit (customizable) | 42U |
| Cabinet Size (mm) | 600 (W) x 1200(D) x 2050(H) |
| Weight | About 180kg |
| Static Load | Up to 2200kg |
| Color | Black or Gray |
| Structure Composition | Welding framework, cabinet seal design as a whole |
| Meet Standard | ANSI/EIA RS-310-D, IEC297-2, DIN41491, DIN41494, GB/T3047.2-92 |
| IP Level | IP5X |
| Display Panel | 10.1” Touch Panel LCD |
| Display Languages | English / Chinese |
| LED Lighting | BI-Color (Red & Blue) |
| Front Door | Toughened glass door with Mechanical lock or fingerprint lock (Support face detector) |
| Rear Door | Sheet metal door |
| Safety Standard | RoHS |

Power Distribution Box

| No. | Parameter | Value |  |
| --- | --- | --- | --- |
| 1 | Input Rated Voltage(V) | 220VAC |
| 2 | Input Rated Current(A) | 80A |
| 3 | Input Switch | 80A /1P |
| 4 | Output Switch | 2*50A/1P+C50A/2P+D20A/1P*2+16A/1P*4 |
| 5 | Lightning Protection Level | Class C lightning protection |  |
| 6 | Dimensions(mm) | W*D*H，483*500*3U |
| 7 | Color | Black, off-white or according to customer's specification |  |
| 8 | Ways To Enter and Exit | Top-in and top-out or according to customer's designation |  |
| 9 | Installation | 19" Rack mounted |  |
| 10 | Cooling | Natural cooling |  |

Precision Air Conditioning

| Rack-Type Air Condition Technical Specification |  |  |
| --- | --- | --- |
| Type |  | 6.5KW |
| Cooling Capacity | Cooling capacity | 6.7 |
|  | Sensible heat ratio(SHR) | 98% |
| Machine air volume (m³/h) |  | 1500 |
| Energy efficiency ratio (EER) |  | 3.5 |
| Compressor | Qty (PC) | 2 |
|  | Type | Enclosed inverter compressor |
| Fans type |  | Hypokinesis EC centrifugal fan |
| Expansion valve type |  | Electronic expansion valve |
| Air supply mode |  | Upper, left, right and three side air supply |
| Evaporator |  | Copper pipe+ Hydrophilic fin |
| Freezing medium |  | R410A |
| Unit standard heating (W) |  | 1000 |
| Power parameter | Input | 220V/50Hz |
|  | Electric power supplying parameters FLA(A) | 16.6(30) |
|  | Recommended air switch model | 32A |
| Pipe type | Self-draining pipe (mm) | Inner p16/Outer p21 |
|  | Strong-Draining pipe (mm) | Inner p5/Outer p7 |
|  | Refrigerant air pipe (mm) | 15.88 |
|  | Refrigerant fluid pipe (mm) | 9.52 |
| Indoor machine size (mm) |  | 440*760*352 |
| Indoor machine weight (kg) |  | 35 |
| Outdoor machine size (mm) |  | 810*580*280 |
| Outdoor machine weight (kg) |  | 35 |
| Connect the inner and outer machines with copper pipes and cables |  | 5m |

UPS（Uninterrupted Power Supply）

| Mode |  | UPS-RM20101-11 |
| --- | --- | --- |
| Power capacity |  | 10kVA/10000W |
| Input | Voltage range | 110-288VAC(220/230/240VAC) |
|  | Frequency | 40-70Hz |
|  | Power factor | ≥0.99 |
| Output | Voltage range | 220VAC±1% |
|  | Frequency | 50/60Hz |
|  | Wave form | Sinusoidal wave |
|  | Power factor | 1 |
|  | Overload capacity (Inverter mode) | 110% : Bypass after 10 minutes; 130% : Bypass is cut after 1 minute; 150% : Bypass after 30 seconds, shut down after 1 minute |
|  | Peak value ratio | 3：1 |
| Efficiency |  | Main road mode 95%； ECO Mode 98% |
| Battery | Mode | Depends on the external battery |
|  | Qty |  |
|  | Maximum charging current | 5A |
|  | Dc voltage | 192-288VDC |
| Communication mode |  | RS 232、SNMP |
| Option |  | Removable dry contact card, maintenance switch, parallel card, battery pack, USB, SNMP, RS 485 interface |
| Bypass |  | Standard configuration |
| Environment | Temperature | 0-40℃ |
|  | Humidness | 0-95% |
| Size |  | 440*550*86 |
| W*D*H(mm) |  |  |
| Special specification |  | Depth of the server cabinet ≥1 m |
| Weight (kg) |  | 18 |

Dynamic Environment Monitoring System

| Item | Technical Specification |
| --- | --- |
| CPU | ARM Cortex A9 Quad-core, Max Frequency 1.2GHz |
| Operating System | Android 5.1 |
| Memory | DDR3L 2GB |
| Flash Rom | 8GB eMMC Flash |
| Standard Serial Port | 2 Ports RS232 |
| Standard Serial Port | 2 Ports RS485 |
| Debug Port | 1 Port Micro USB |
| Digital Input Port | 2 Ports DI |
| Digital Output Port | 2 Ports DO(for relay control) |
| USB Port | 3 Ports (1 Port USB Host, 2 Ports USB Device) |
| Debug Port | 1 Port Micro USB |
| Output Supply | 6 Ports 12V/1A |
| Wireless | Reserved for 3G, 4G and Wi-Fi module expansion slot |
| Ethernet | 1 Ports RJ45 10M/100M/1000M |
| Operating Voltage | 12V DC |
| Max Power | 35W |
| Size | 266 mm× 182 mm× 48.5 mm |
| ESD Level | Contact: 6KV; Air: 8KV |
| MTBF | ≥100000H |
| Operating Temperature | -20~60℃ |
| Operating Humidity | 10%~90%RH |

Battery Pack

Battery Pack                        Valve Regulated Lead Acid Battery (VRLA)

| Cabinet Power | Backup Time | Battery Pack Type | Battery Pack QTY |
| --- | --- | --- | --- |
| 10KVA (9kw) | 15 mins | 5U Battery Pack (8pcs 38AH) | 2set |

PDU（Power Distribution Unit）

| Item | Specification |
| --- | --- |
| Rated current | 16A |
| Rated voltage | 220VAC 50/60Hz |
| Output ports | 24*C13 |
| Max power | 5KW |
| Outline size | 1217(Adjustable length) x 44 x 44 mm |
| Installation method | Horizontal/Vertical installation |
| Safety certification | UL/CE/CCC |
| Function | Lightning protection, intelligent monitoring, and general circuit breaker are optional |

Integrative Door Lock

| Type of Device | Specification |
| --- | --- |
| Rated operating voltage | DC12V |
| Working current | Static standby: <250mA Dynamic Electronically Controlled Unlocking: <500mA |
| Communication mode | RS485，9600bit/s |
| Service life | Above 500,000 times |
| Color | Black |
| Operating temperature/humidity | -20℃ ~50℃ / 20～90% |
| Storage temperature/humidity | -30℃ ~60℃ / 20～90% |
| IP rate | IP65 |
| 3 unlock modes | Remote unlocking by monitoring host control software Authorized card writes the card number and swipes card to unlock Mechanicals unlock |
| Access control authorization | 500 to 5000 fingerprints |
| Authorized entrance number | Up to 5000 |
| Software authorization | Authorized by system software through network Communication |
| Event records | Up to 1120 history records |
| Function | Mechanical unlocking, password of the IC card, fingerprint and so on, can be paired with |
| Communication interface | RS485 networking real-time monitoring, door status, handle status, real-time clock function |

Server-Rack Automatic Fire Suppression System (Option)

| Type Of Device | Server-Rack FireSuppression Unit |
| --- | --- |
| Model number | JJQR-Q-W/C-4/1.2-WL/ZZ |
| Control the number of cabinets | Less than 4 set |
| Size | 483(W)*500(D)*1U(H)mm |
| Fire extinguishing agent | HFC-ea. |
| Storage pressure(20℃) | 1.2MPa |
| Injection time | ≤10S |
| Action temperature of fire detecting tube | 170 ℃ ±10 ℃ |
| Max. Length of Fire detection tube | 5m for each cabinet |

Product Configuration

| PN | Description | Picture |
| --- | --- | --- |
| MDC-5331-1122-C141-1351 | Triplex cabinet KHIPU MDC: 3 set Close Cabinet 42U: 600mm x 1200mm x 2050mm 1 set UPS capacity is 10KVA 1-phase 15-minute Battery Pack 1 set Panel Distribution Box 1 Phase 2 set Precision Air Cooling 6.5 KW 3 pcs Smoke sensor 3 pcs Temperature & Humidity Sensor 3 pcs PDU 24 outlet PDU, 16A, IEC 320 C13 3 pcs Keypad, Fingerprint lock 3 set Automatic fire suppression system 1 set Master Environmental Monitoring System bundling with Touch Panel LCD for Dashboard |  |

Note: The above product information is the default information and can be customized according to customers.

GLOBAL FOOTPRINT

| Headquarters | South Asia | South East Asia | East Asia |
| --- | --- | --- | --- |
| Donauwörth - Germany PROSE Technologies GmbH Add.: Dr.-Friedrich-Drechsler-Straße 14, 86609 Donauwörth, Germany E-mail: info.eu@Prosetechnologies.com | Mumbai - India PROSE Technologies India Private Limited Add.: 403-407, Eco Star, Vishveshwar Nagar, Goregaon East, Mumbai ,India 400063 Tel: +91 22-66453000 E-mail: info.in@prosetechnologies.com Pune - India PROSE Technologies India Pvt.Ltd Add.: A-79, Block-A , Horizon Industrial Parks, Phase II, MIDC Chakan Industrial Area, Khed, Pune , India 410501 Tel: +91 2135-635200 E-mail: info.in@prosetechnologies.com Bangalore - India PROSE Technologies India Private Limited Add.: No.494 East End Main Road, Jayanagar IX Block, Bangalore, India 560069 E-mail: info.in@prosetechnologies.com New Delhi - India PROSE Technologies India Pvt.Ltd Add.: H-3/157, 2nd Floor, Vikas Puri, New Delhi, India 110018 E-mail: info.in@prosetechnologies.com Dhaka - Bangladesh PROSE Technologies (Bangladesh) Limited Add.: House-360 (2nd Floor), Lane-5 (East), Baridhara DOHS, Dhaka-1206, Bangladesh Tel: +880 1977070130 E-mail: info.bd@prosetechnologies.com Islamabad - Pakistan Add.: Unit 514, 5th Floor, ISE Towers, Islamabad, Pakistan Tel: +92 3335357733 E-mail: info.pk@prosetechnologies.com Sri Lanka Tel: +880 1977070130 E-mail: info.lk@prosetechnologies.com | Selangor - Malaysia PROSE Technology (M) Sdn. Bhd Add.: Unit 2-1, Level 2, The Podium, Tower 3, UOA Business Park, No 1, Jalan Pengaturcara U1/51a, Seksyen U1, 40150 Shah Alam, Selangor, Malaysia Tel: +60 126859319 E-mail: info.my@prosetechnologies.com Bangkok - Thailand PROSE Technology (Thailand) Co., Ltd Add.: 349 SJ Infinite I Business Complex,9 Floor, Room 905, Vibhavadi Rangsit Road, Chom Phon Sun-district, Chatuchak District, Bangkok Provice, Thailand Tel: +66 80 6606630 E-mail: info.th@prosetechnologies.com Singapore PROSE Technologies (Singapore) Pte.Ltd Add.: 10 Anson Road#13-15 International Plaza Singapore 079903 Tel: +6598366793 E-mail: info.sg@prosetechnologies.com Hanoi - Vietnam PROSE Technologies (Vietnam) Company Limited Add.: Floor 15, Vinaconex 9 Building, HH-2 Block, Pham Hung Street, Me Tri Ward, Nam Tu Liem District, Hanoi, Vietnam Tel: +84 933086498 E-mail: info.vn@prosetechnologies.com Taguig - Philippines PROSE Technologies Philippines, Inc. Add.: Unit 17 19th Floor Highstreet South Corporate Plaza Tower 1, 26th Street corner 9th Avenue, Bonifacio Global City, Taguig City, Philippines Tel: +63 27572762 E-mail: info.ph@prosetechnologies.com Jakarta - Indonesia PT. PROSE Technologies Indonesia Add.: Plaza Sentral 6th Floor, Jalan Jenderal Sudirman No. 47, Jakarta 12930, Indonesia Tel: +62 21 57901997 E-mail: info.id@prosetechnologies.com | Suzhou - China PROSE Technologies (Suzhou) Co.,Ltd Add.: No. 6, Shen’an Road, DianShanHu, Suzhou, JiangSu, China E-mail: Info@prosetechnologies.com Beijing - China PROSE Technologies (Beijing) Co.,Ltd E-mail: Info@prosetechnologies.com Shanghai - China PROSE Technologies (Shanghai) Co.,Ltd E-mail: Info@prosetechnologies.com Dongguan - China Add.: Room 1506, building 1, No. 1, Yile Road, Songshanhu Park, Dongguan City, Guangdong Province, China E-mail: Info@prosetechnologies.com Hongkong - China PROSE Technologies Company Limited Add.: Unit B 13/F,Prat Commercial Building, 17-19 Prat Avenue, Tsimshatsui, Kowloon, HongKong, China Tel:+86 512 86896789 - 2921/2922 E-mail: info.hk@prosetechnologies.com Taiwan Tel: +63 2 7572762 E-mail: info.tw@prosetechnologies.com |
| Western Europe |  |  |  |
| Dublin - Ireland PROSE Technologies (Ireland) Limited Add.: 6th Floor, South Bank House, Barrow Street, Dublin 4 Ireland E-mail: Info@prosetechnologies.com |  |  |  |
| Eastern Europe & Central Asia |  |  |  |
| E-mail: info.eeca@prosetechnologies.com |  |  |  |
| North America |  |  |  |
| New Jersey - America PROSE Technologies LLC Add.: 550 Clark Drive Budd Lake, NJ 07828, United States of America Tel: +1 888 840 4066 E-mail: info.us@prosetechnologies.com |  |  |  |
| Middle East |  |  | Oceania |
| Dubai - UAE PROSE Technologies DMCC Add.: 3702, Mazaya Business Avenue BB2, JLT, Dubai Tel: +971 4 3999168 E-mail: info.ae@prosetechnologies.com |  |  | New South Wales - Australia PROSE Technologies (Australia) Pty. Ltd Add.: 5/13 Boundary Rd, Northmead, NSW 2152, Australia Tel: +61 2 78055523 E-mail: info.au@prosetechnologies.com |
| Africa |  |  |  |
| Nairobi - Kenya PROSE Technologies Africa (PTY) Ltd Tel: +254 780440410 E-mail: info.ke@prosetechnologies.com Gauteng, (Johannesburg) - South Africa PROSE Technologies Africa (PTY) Ltd Add.: Building 20, Cambridge Office Park, 5 Bauhina Road, Highveld Techno Park Centurion, Gauteng 0169, South Africa Mobile: +27 725554840 E-mail: info.za@prosetechnologies.com |  |  |  |